## Slide 1
ORV3 Power Shelf
Development Update (Liteon)

## Slide 2: ORV3 Power Shelf Development Update Lam Vu, Director of Engineering, Liteon Technologies
R&P (Rack & Power)

## Slide 3: PSU Specification
Input Voltage:
  200V to 277V +/- 10%, 47Hz – 63Hz
  Max input current: 18A
  20mS hold-up time
  Power Factor:
    >0.98 @ 30% to 100% load
    > 0.95 @ 10% to 30% load
  THD: < 5% @ > 30% load
  Efficiency: 97.5% peak incl. fan loss
  Operating temperature range: 0 – 45C

## Slide 4: PSU Specification
Output Voltage
  Main output: 51V +/- 0.25% setpoint
  3000W
  Dynamic Response: +/- 1V in addition to droop voltage
  Current Share: < 3% @ load > 40%
    Voltage droop: 0.5V over full load current
    Active current share
  Output isolated from chassis ground
No aux. output
Communication:
  PMBus on I2C hardware
  Modbus RS-485

## Slide 5: PMC Specification
Communicate with PSU via I2C or Modbus
Communicate with Rack Management System
  Web Interface
    HTTP/HTTPS RESTful API
    Redfish v1
    SNMP v3
    IPMI BMC
  Modbus (RS485/TCP)
  Remote FW Upgrade (PSC/PSU)

## Slide 6: ORV3 PSU Models at Liteon
Liteon develops a whole range of power supply module under ORV3 specification
PSU for 21” rack application:
  3kW in 520mm length
  5kW in 520mm length
  5.5kW in 640mm length
PSU for 19” rack application:
  3kW in 68mm width, 520mm length
  39mm height to fit into 1RU power shelf
  Shelf controller (PMC) mounted in rear of power shelf

## Slide 7: ORV3 Power Shelves at Liteon
Liteon can customize shelf configuration using ORV3 power supply for different application:
  Single or dual AC inputs: 208V ∆, 240V ∆, 415V Y, 480V Y
  OU height 21” OCP power shelf
  RU height 19” power shelf
  Shelf with auxiliary C13s for TOR components
  Shelf with daisy chain signal connector for parallel between shelves
  Immersion liquid cool power shelf with front access

## Slide 8: 1OU Power Shelf

## Slide 9: 2OU Power Shelf

## Slide 10: 1RU Power Shelf
PSU |  |  |  | Shelf |  |  | Case sheet metal thickness |  | 
Length | Width | Height | Slot quantity | Length | Width | Height | Case-btm | Case-top | Partition
520 | 68 | 39.55 | 6 | 727 | 445 | 43.65 | 1.2 | 1 | 1
PSC width |  |  |  |  |  |  | 
21.6 |  |  |  |  |  |  | 

## Slide 11: Immersion Application Power Shelf: All Front Access

## Slide 12: BBU Specification
Battery string:
  Murata VCT4, 11S6P
  Capacity: 4 minutes at the end of 4 years, 35C ambient
  Voltage range: 33V – 44V
  Max charging current: 5A (3hr charging time)
  > 10 days between recharge (self discharge)
  BBU life: 8 years

## Slide 13: BBU Specification
Output Voltage
  Main output: 48V +/- 0.25% setpoint
  3000W
  Efficiency:
    44V input: 99% pk, 98.4% full load
    34V input: 98.7% pk, 97.3% full load
  Dynamic Response: +/- 1V in addition to droop voltage
  Current Share: < 3% @ load > 40%
    Voltage droop: 1V over full load current
    Active current share
  Output isolated from chassis ground

## Slide 14: BBU Shelf

## Slide 15: More Power in a Rack: Current Sharing Between Power Shelves

## Slide 16: More Power in a Rack: Current Sharing with Droop Only
  Without active current share signal, two power shelves can share thru droop with more error between two shelves: < 10%
Current Sharing with Droop Only |  |  |  |  |  |  |  |  |  |  |  | 
 | PSU_1 |  | PSU_2 |  | PSU_3 |  | PSU_4 |  | PSU_5 |  | PSU_6 | 
 | shelf 1 | shelf 2 | shelf 1 | shelf 2 | shelf 1 | shelf 2 | shelf 1 | shelf 2 | shelf 1 | shelf 2 | shelf 1 | shelf 2
120A | 9.31 | 11.56 | 9.35 | 12.27 | 9.79 | 8.19 | 8.33 | 11.73 | 8.18 | 11.61 | 7.87 | 11.27
240A | 18.79 | 21.47 | 19.37 | 21.99 | 19.79 | 18.27 | 18.06 | 21.59 | 18.72 | 21.46 | 17.61 | 21.22
360A | 28.91 | 31.53 | 29.25 | 31.97 | 30.36 | 28.68 | 27.79 | 31.72 | 28.42 | 31.40 | 27.96 | 31.61
480A | 38.77 | 41.39 | 38.58 | 41.56 | 40.20 | 38.73 | 37.61 | 41.89 | 37.91 | 41.19 | 37.58 | 41.51
600A | 48.42 | 51.46 | 48.09 | 51.40 | 49.79 | 48.80 | 47.45 | 52.30 | 47.76 | 51.46 | 47.22 | 51.46
720A | 58.13 | 61.24 | 57.61 | 61.14 | 59.87 | 58.98 | 57.03 | 62.52 | 57.34 | 61.25 | 56.54 | 62.02

## Slide 17: Power Transition Between ORV3 PSU Power Shelf and BBS Line Loss
Power Shelf drops output 3V to trigger Battery shelf to start providing power
Power shelf and battery shelf share current by droop mode during transition time
Battery Shelf to Power Shelf
Power Shelf to Battery Shelf
50mS/div
Holdup time
50A/div
Battery Shelf Curr
Power Shelf Curr

## Slide 18: ORV3 Rectifier to BBU Transitions in Fault Cases
One Line of 3-phases fails causing loss of 2 PSUs
120% overload on the remaining 4 PSUs
At the end of overload duration, PSUs lower output by 3 V to signal transferring load to Battery Backup
Battery Shelf supports load

## Slide 19: For more information & Prototypes
Contact: jason.yang@liteon.com

## Slide 20: Call to Action
RACK & POWER
Get in touch with us to receive latest information about the ORV3 power shelves
Start testing the ORV3 Power Shelves by yourself! Samples available!
Give feedback of your findings to help improving the project in future

## Slide 21
Thank you!