## Slide 2: Takeaways after two years of Immersion Michaël HELEZEN, Research Engineer, 2CRSi mhe@2crsi.com
ACS

## Slide 3: Outline
ADVANCED COOLING SOLUTIONS
Introduction
Material compatibility
Mechanical and thermal
Electrical
Software
Conclusion

## Slide 4: Introduction
ADVANCED COOLING SOLUTIONS
2CRSi group is designing and manufacturing servers
In order to provide more energy-efficient solutions, 2CRSi started designing servers specifically for immersion cooling two years ago

## Slide 5: Material compatibility
ADVANCED COOLING SOLUTIONS
Thermal paste for CPU or GPU :
Test
Indium Foil
Processor case potentially not compatible with immersion Tests in progress

## Slide 6: Material compatibility
ADVANCED COOLING SOLUTIONS
Cables compatibility (Network or power) in dielectric liquid
incompatibility possible between cable / liquid
Example of Cables connection in immersion
standard fiber optics not compatible within immersion
cables stiffens with liquid

## Slide 7: Material compatibility
ADVANCED COOLING SOLUTIONS
Issues with labels and warranty implication
In immersion, glued labels may peel off, driving :
 tank cleanliness modification
 difficult components identification
 warranty implications
Alternative solutions
plastified label
cover the label with transparent epoxy resin

## Slide 8: Mechanical and thermal
ADVANCED COOLING SOLUTIONS
Position of components in the server
According to the typology of convection (natural or forced):
Key principle:
Hottest components at the bottom of the tank and the coldest at the top
Direction of heating flow
Heatsink fins parallel with heat flow
Do not block the movement of the liquid

## Slide 9: Mechanical and thermal
ADVANCED COOLING SOLUTIONS
Servers cooling
Location of the chassis in the tank -> facilitate the thermal flow
Temperature evolution after cooling shut down

## Slide 10: Mechanical and thermal
ADVANCED COOLING SOLUTIONS
Specific to submerged servers
Fixing suitable for submerged components
Use of hex socket screws  metal chips
Chassis reinforcement for easier extraction
Handles added to servers

## Slide 11: Electrical
ADVANCED COOLING SOLUTIONS
Change of environment for electrical components
Physical properties between air and dielectric liquids are different (ex : electrical permittivity or conductivity) and could change passive values of components.
To be assessed
Homogeneity of temperature of the components :
service life improvement
failure rate reduction
risk to be identified -> temperature too high for specific components

## Slide 12: Electrical
ADVANCED COOLING SOLUTIONS
Immersion of Power supply units
Electrical relay  must be sealed
Capacitor chemically compliant
Thermal paste
Turn off the fans
Tests PSUs
test device for PSU
Inflated capacitor
capacitor
disconnect the fan and add a fan simulator

## Slide 13: Software for PSU
ADVANCED COOLING SOLUTIONS
By changing the firmware in the PSU, we can:
Deactivate the fan and prevent a fault signal
Ensure weak ventilation for test in air / turn it off in immersion
Modify the Over Temperature Protection (OTP) to adapt to immersion

## Slide 14: Conclusion
ADVANCED COOLING SOLUTIONS
After two years working with immersion, 2CRSi wanted to share with the OCP community our experience, the specifics of the servers made for immersion observed
So, in conclusion, there are many points to consider when immersing servers in a dielectric liquid but once they are mastered, there is no problem to use immersed servers.
We know that by taking the appropriate precautions, it is possible to transpose the majority of air servers to immersion
That is why, we are confident in immersion cooling technology for its main advantages like significant money savings, component failure rate reduction, components life cycle increase or IT densification.

## Slide 15: Call to Action
Project Wiki with latest specification : https://www.opencompute.org/wiki/Rack_%26_Power/Advanced_Cooling_Solutions
We are participating and will continue to participate in the OCP project:
Rack and power / advanced Cooling solutions.
You can find a lot of information on immersion and several practical guides with the link below.
If you have any questions about immersion, feel free to ask questions of members of this group or ourselves and we will be happy to help.